POLICIES AND PROCEDURES

FOR

THE CONTROL OF HAZARDOUS ENERGY

TAGOUT/LOCKOUT

FACILITIES MANAGEMENT DEPARTMENT

JANUARY 8, 1998

I.	SCOPE

This procedure covers the servicing and maintenance of machines and equipment in which the unexpected energization or start-up of the machines or equipment, or release of stored energy could cause injury to employees and/or equipment.  This procedure establishes adequate performance requirements for the control of hazardous energy.

II.	PURPOSE

This procedure establishes the minimum requirements for the tagout/lockout of energy isolating devices whenever maintenance or servicing is done on machines or equipment.  It shall be used to ensure that the machine or equipment is stopped, isolated from all potentially hazardous energy sources and is tagged/locked out before employees perform any servicing or maintenance upon that machine or equipment where the unexpected energization or start-up of the machine or equipment or release of stored energy could cause bodily injury or equipment damages.

III.	COMPLIANCE

All employees are required to comply with the restrictions and limitations imposed upon them during the use of the tagout/lockout procedures.  Authorized employees are required to perform the tagout/lockout activities in accordance with this procedure.  All employees, upon observing a machine or piece of equipment which is tagged/locked out, shall not attempt to start, energize or use that machine or equipment.

The procedures identified in this document conform to the Federal Occupational Safety and Health Administration requirements.  Reference for this procedure is Federal OSHA, Title 29 CFR, Chapter XVII, Section 1910.147.  Failure to use the tagout/lockout procedures and rules contained herein or any violation of these procedures shall be cause for disciplinary action.

IV.	DEFINITIONS

Affected Employee:  An employee whose job requires him/her to operate 	or use a machine or equipment on which servicing or maintenance is 	being performed under tagout/lockout, or whose job requires him/her to 	work in an area in which such servicing or maintenance is being 	performed.

Authorized Employee:  A person who tags/locks out machines or equipment 	in order to perform servicing or maintenance on that machine or equipment.  An 	affected employee becomes an authorized employee when that employee’s 	duties include performing servicing or maintenance covered under this section.

Capable of Being Locked Out:  An energy isolating device is capable of being locked out if it has a hasp or other means of attachment to which, or through which, a lock can be affixed, or it has a locking mechanism built into it.  Other energy isolating devices are capable of being locked out, if lockout can be achieved without the need to dismantle, rebuild, or replace the energy isolation device or permanently alter its energy control capability.

Energized:  Connected to an energy source or containing residual or

stored 	energy.

Energy Isolating Device:  A mechanical device that physically prevents the 	transmission or release of energy, including but not limited to the following:  A 	manually operated electrical circuit breaker; a disconnect switch; a manually 	operated switch by which the conductors of a circuit can be disconnected from all 	ungrounded supply conductors, and, in addition, no pole can be operated 	independently; a line valve; a block; and any similar device used to block or 	isolate energy.  Push buttons, selector switches and other control circuit type 	devises are not energy isolating devices.

Energy Source:  Any source of electrical, mechanical, hydraulic, pneumatic, 	chemical, thermal, or other energy.

Hot Tap:  A procedure used in the repair, maintenance and services activities 	which involves welding on a piece of equipment (pipelines, vessels or tanks) 	under pressure, in order to install connections or appurtenances.  It is commonly 	used to replace or add sections of pipeline without the interruption of service for 	air, gas, water, steam, and petrochemical distribution systems.

Lockout:  The placement of a lockout device on an energy isolating device, in 	accordance with an established procedure, ensuring that the energy isolating 	device and the equipment being controlled cannot be operated until the lockout 	device is removed.

Lockout Device:  A device that utilizes a positive means such as a lock, either 	key or combination type, to hold an energy isolating device in a safe position and 	prevent the energizing of a machine or equipment.  Included are blank flanges 	and bolted slip blinds.

Normal Production Operations:  The utilization of a machine or equipment 	to perform its intended production function.

Servicing and/or Maintenance:  Work place activities such as constructing, 	installing, setting up, adjusting, inspecting, modifying, and maintaining and/or 	servicing machines or equipment.  These activities include lubricating, cleaning 	or unjamming of machines or equipment and making adjustments or tool 	changes, where the employee may be exposed to the unexpected energization 	or start-up of the equipment or release of hazardous energy.

Setting Up:  Any work performed to prepare a machine or equipment to 	perform its normal production operation.

Tagout:  The placement of a tagout device on an energy isolating device, in 	accordance with an established procedure, to indicate that the energy isolating 	device 	and the equipment being controlled may not be operated until the tagout 	device is removed.

Tagout Device:  A prominent warning device, such as a tag and a means of 	attachment, which can be securely fastened to an energy isolating device in 	accordance with an established procedure, to indicate that the energy isolating 	device and the equipment being controlled may not be operated until the tagout 	device is removed.

White Personal Danger Tag:  The white personal danger tag is a tag which 	shall be used only for the protection of personnel.  Each authorized employee 	shall use his/her own white personal danger tag.  Each white personal danger 	tag shall bear the individual’s name and be suitably protected against destruction 	of harsh environments.

Yellow Equipment Danger Tag:  The yellow equipment danger tag shall be 	used for the protection of equipment only.  The yellow equipment danger tag 	indicates that the particular machine or equipment must not be energized.  The 	yellow equipment danger tag IS NOT to be used as a white personal danger tag.

V.	SEQUENCE OF TAGOUT/LOCKOUT

A.	The authorized employee intending to perform maintenance or serving 	shall notify all affected employees that servicing or maintenance is 	required on a machine or equipment and that the machine or equipment 	must be shut down and tagged/locked out to perform the servicing or 	maintenance.

B.	The authorized employee shall identify the type and magnitude of the 	energy that the machine or equipment utilizes.  The authorized employee 	shall be required to understand all hazards of the energy and shall know 	all the methods to control all of the energy sources.

C.	If the machine is operating, the authorized employee or the affected 	employee shall shut down the machine or equipment by normal operating 	means.  This can be accomplished by various methods but should in all 	cases consist of recommended practices.

D.	Once the machine or equipment is stopped by normal means, or if the 	machine or equipment is already at rest, the authorized employee shall 	de-activate the energy isolating device (s) so that the machine or 	equipment is isolated from all energy sources.

E.	Tagout/lockout the energy isolating devices.

F.	Stored or residual energy such as that in capacitors, springs, elevated 	machine members, rotating flywheels, hydraulic systems, air pressure, 	water pressure, gas, steam, etc. must be dissipated or restrained by 	methods such as grounding, repositioning, blocking, bleeding down, etc.

G.	Ensure that the machine or equipment is disconnected from all energy 	sources by first checking that no personnel are exposed to the machine’s 	operation.  Verify the isolation of the equipment by operating the push 	button or other normal starting device of the machine or equipment.  Make 	certain that the machine or equipment will not operate.

CAUTION:  Be sure to return any operating device or starting switch 	to its “neutral” or “off” position after making the above safety check.

H.	The machine or equipment is now properly tagged/locked out.

VI.	SEQUENCE OF RESTORING EQUIPMENT TO DUTY

A. 	When servicing or maintenance is complete and the machine or 	equipment is ready to be returned to the service, check for tools and other 	service items, which may have been inadvertently left in the work area.  	Clear the area of any debris left from servicing.

B.	Notify all affected employees that serving or maintenance is complete and 	that the machine or equipment is ready to be returned to duty.  All 	authorized employees must be advised of the service or maintenance 	completion.  Check the work area to ensure that all employees have been 	safely positioned or removed from operating areas.

C.	Verify that the controls are in the “neutral” or “off” position.

D.	Remove the tags and locks from the tagout/lockout devices and re-	energize the machine or equipment.

E.	Report to affected employees that the tagout/lockout has been removed 	and that the machine or equipment is ready for use.

VII.	RULES FOR DANGER TAG USE

A.	WHITE PERSONAL DANGER TAGS

1.	When more than one type of work is being performed on a machine 		or equipment at the same time and different crafts are involved, 			each authorized employee from each craft shall attach a white 			personal danger tag to the isolating device (s).

2.	When a white personal danger tag is placed on an isolating device 			for group protection, the authorized employee who places the tag 			shall become responsible for the well being of all authorized 				employees working under his/her protection.

3.	A white personal danger tag shall be removed only by the 				authorized employee who placed the tag on the isolating device 			(note one exception to this below).  The white personal danger tag 			shall remain on the isolating device as long as the authorized 			employee is on the job or until the authorized employee leaves the 			job site for the day or work shift.

4.	If a white personal danger tag is left attached to an isolating device 			after an authorized employee has completed the service or  				maintenance and the authorized employee has left the job site, the 			supervisor of the authorized employee may remove the white 			personal danger tag only if all of the following conditions are met:

a.	All efforts to contact the authorized employee 				have failed.

b.	The supervisor is sure that service or maintenance is 			completed and that the machine or equipment is 			ready for use.

c.	The supervisor is sure that all other authorized and 			affected employees are clear of the normal operation 			of the machine or equipment.

5.	If an authorized employee has been working on a machine or 			equipment and must leave the job site before the equipment is 			ready for duty, the authorized employee must remove his white 			personal danger tag and place a yellow equipment tag on the 			isolating device (See yellow equipment danger tags below).

B.	YELLOW EQUIPMENT DANGER TAGS

1.	The yellow equipment danger tag must be filled out completely 			indicating the name of the affected or authorized employee, the 			date and time the tag was placed and the reason for placing the 			tag. THIS TAG IS FOR EQUIPMENT PROTECTION ONLY.

2.	A yellow equipment danger tag may be removed by a competent 			and authorized or affected employee as long as there is assurance 			that the machine is in proper running condition.  Every effort must 			be made to ensure that the machine or equipment has been 				serviced and/or repaired so that it can be placed into operation 			without undue concern.

- The yellow equipment danger tag must be returned to the

originator of the tag so that a record of the machine’s disposition

can be traced.