CONFINED SPACE PROGRAM

I.	INTRODUCTION

This procedure is designed to protect Indiana University of Pennsylvania 	(IUP) employees from injury where their job duties require entry into 	confined spaces.

Periodically, confined spaces must be entered for inspection, cleaning, or repair.  Since these spaces can store materials that are flammable, toxic, corrosive, or oxygen consuming, entry can be dangerous.  To avoid accidents caused by entries into improperly prepared confined spaces, the “Confined Space Entry Procedure” has been developed.

DEFINITION:  A confined space is any area not intended for human occupancy and that also has the potential for containing or accumulating a dangerous atmosphere.  The area may permit either the accumulation of hazardous gases, mists, fumes, vapors, dust, or the possibility of an oxygen deficiency.  In addition, the means of egress may be restricted to such a degree that a person would have difficulty escaping in an emergency.

Examples of confined spaces on the IUP campus include:

Storage tanks, open pits, sewers, manholes, towers, and pipe tunnels.

A minimum of safety steps must be completed before entry into the confined space can begin.  These steps can be categorized under three general areas:

1.  Preparation of the confined space prior to entry.

2.  Safety requirements for entry.

3.  Emergency rescue procedures.

Each area, vital to the development of a safe confined space entry procedure, will be discussed.

II.	PREPARATION OF THE CONFINED SPACE PRIOR TO ENTRY

The following five steps must be completed before a confined space is safe to enter:

1.  Conditioning

2.  Ventilating

3.  Isolating

4.  Immobilizing power equipment

5.  Testing the confined space atmosphere

A.	Conditioning the confined space

1.	Before entering the confined space, empty (pump out or drain) all 	material in it as completely as possible.  If this is not possible, the 	supervisor in 	charge of the work being done shall consult with the 	safety office to discuss alternatives.

2.	If chemicals are present (i.e. storage tanks), flush the confined 	space with water or an appropriate cleaning solution and follow with 	a final water flush.  It may be necessary to fill the space with water 	and to boil the water to soak out or deactivate certain chemicals.

3.	If flammable or toxic gases are present, purge the confined space 	with air after washing.

- After the pressure in the confined space is at ambient pressure,

the space is then conditioned and can be opened.  All covers should be removed.

B.	Ventilating the confined space

1.	Mechanical ventilation of the confined space can now be started.  	This can be accomplished by introducing fresh air into the confined 	space with a 	powered blower.

2.	Ventilation of the confined space must continue until all pockets of 	“dead 	air” which may contain toxic, flammable, or inert gas have 	been eliminated and measurement establishes that there is 	sufficient oxygen in and around the confined space (not less that 	20.8%) and that the air is free of any explosive or toxic mixture.  	Additional measurements 	must be conducted at 15-minute 	intervals during operations.

3.	Only air should be used for ventilation, never nitrogen or oxygen.

C.	Isolating the confined space

1.	Isolate the confined space by blocking off all pipes through which 			the toxic or potentially harmful materials can be introduced into the 			confined space.  Include ALL liquid, gas, and vapor lines.  Note:  			not all steams lines can be isolated at all times in the pipe tunnel  			or manholes.

2.	The following are two general methods of isolation:

a.	The preferred method is total mechanical which includes:

1.	Blanking off the entering line by using in-line or 					individual blinds which are often referred to as “skillet” 				or spectacle blinds.

2. 	Disconnecting pipes and closing the open ends with 					pipe caps, plugs, or blind flanges.

3.	Removing a section of the pipe.

b.	The other isolation method is the double block and bleed.  				This method may only be used on water and steam lines and 			must be approved by the plumbing supervisor.  The use of 				this technique is discouraged since it does not create a 				positive break between the confined space and the supply 				line.  If this method is used, the two line valves must be 				chained, locked and tagged when the in the closed position.

3.		Where discharge lines from relief valves enter the confined 				space, they must be disconnected and temporarily vented to 				a safe location.

D.	Immobilizing power equipment

Whenever a confined space is equipped with power driven internal 			equipment, such as mixers, agitators, or conveyors, this equipment 			must be immobilized before entry is allowed.

This is accomplished by following the University lockout/tagout 			procedure.

E.	Testing the atmosphere of the confined space

1.	After all of the previous procedures for preparation of the confined 			space 	for entry have been completed, the confined space 				atmosphere shall be tested by the safety observer and entrants and 		monitored continuously while work is in progress.  The safety 			observer will record readings every 15 minutes.

2.	The confined space atmosphere shall be tested by the safety 			observer and entrants for the following:

a.	Oxygen deficiency – Test for oxygen.  If the atmosphere in 				the confined space is less than 20.8% oxygen, purge with air 			until sufficient oxygen is present.  A test for oxygen content 				must be carried out in all cases of confined space entry, 				regardless of previous contents or prior preparation of the 				confined space.

b.	Flammable vapors and gases – Test for possible flammable 				vapors and gases that could be present.  If the atmosphere 				is flammable, purge with air and retest until atmosphere is 				safe.  Additional measurements should be recorded at 15-				minute intervals while work is in progress.

c.	Hydrogen Sulfide – Test for H2S.  If test levels exceed the 				established threshold limit values (TLVs), ventilation 					procedures must be continued until levels are below the TLV 			before anyone can enter the confined space.

d.	Carbon Monoxide – Test for CO.  If test levels exceed the 				established threshold limit values (TLVs), ventilation 					procedures must be continued until levels are below the TLV 			before anyone can enter the confined space.

III.	SAFETY REQUIREMENT FOR ENTRY

A.	Safety Observer:

This procedure requires that a safety observer be present wearing 			the appropriate personal protective clothing, having available:  a 			meter, tripod with retrieval line, blower and radio.

The duties of the safety observer are:

a.	Perform radio test with Campus Police before work 					begins at every confined space.

b.	Ensure safety and retrieval equipment is set up and 					ready for use.

c.	Keep continuous visual and voice contact with the 					people inside the confined space.

d.	Assist in necessary equipment changes.

e.	Ensure that rubber coated, explosion proof extension 					cords along with ground fault circuit interrupters are 					used with power tools, including electric lights.

f.	Respond to any unusual behavior of the people inside 				the confined space.

g.	Protect entrant from external hazards.

h.	Continuously monitor atmosphere and record results 					every 15 minutes.

i.	Ensure that all torches and electrodes are removed 					from the confined space when not in use.

B.	Entrants:

Any person entering the confined space must wear personal 				protective clothing and equipment that is appropriate for the work 			being performed and the condition of the confined space.  Wearing 			appropriate safety equipment is mandatory for every person who 			enters a confined space and for people who are assigned to be 			safety observers.

Appropriate safety equipment may include:

Two-piece rain suit, rubber gloves, rubber boots, face shield or 			hood, fire extinguisher, first aid kit, hard hats, ground fault circuit 			interrupter, body harness, and a mechanical means of retrieval.  			Lifelines should be attached to a fixed object outside of the 				confined space.

C.	Unit Supervisor:

The unit supervisor will ensure that all materials and equipment are 			available, the safety equipment is in proper working order, the 			space has been tested, radio communications completed, and the 			entry permit is completed.  The supervisor will also ensure that all 			safety measures, including any extra measures deemed necessary, 		are followed.

D.	Unit Manager:

The unit manager will discuss the procedures and scope of work 			with the unit supervisor.

IV.	CONFINED SPACE ENTRY PERMIT

NOTE:  A CONFINED SPACE ENTRY PERMIT IS REQUIRED BEFORE ENTERING ANY CONFINED SPACE.

A.	Responsibilities

1.	Unit supervisor:

After checking the job to see that all safety measures and all 				fire prevention precautions have been taken, the supervisor 				has the prime responsibility of completing the Confined 				Space Entry Permit, which he will sign.

2.	The entrants performing the work shall handle the 					equipment safely and use it as to not endanger lives

and property.

3.	The safety observer will assist in preparing the area and 				remain in continuous contact with entrants.

*The entrants and safety observer will sign the permit 					certifying that they have been instructed in the proper 					confined space entry procedures.

4.	The unit manager will discuss the scope of the job to be 				performed with the supervisor that and ensure confined 				space 	permit is completed.

B.	Procedure

1.	The employee wanting a confined space entry permit shall 				first contact the unit supervisor for permission to perform

the work.  If it is necessary to burn or weld in the confined space 	to perform the work, extra work precautions must also be followed.

2.	After receiving permission from the unit supervisor to 					proceed with the work, the safety observer and entrants will 				prepare the equipment and/or area for a confined space 				entry permit.

3.	After completing the permit, the unit supervisor will review to 				ensure that all permit requirements have been satisfactorily 				completed.  The safety observer and entrants will perform 				the atmosphere tests to rule out any explosive, flammable, 				oxygen deficient or toxic atmospheres in the area.  After the 				inspection and atmosphere test, the unit supervisor shall 				certify that all of the safety precautions listed on the permit 				have been considered and will sign the permit in the space 				granting the permit.

V.	EMERGENCY RESCUE PROCEDURE

Emergency Rescue will not be performed by the Indiana Fire and Rescue 	Squad.  The safety observer must not enter the confined space.  Use 	radio to notify campus police in the event of an emergency.  *Refer to

the  Confined Space Emergency Rescue Procedure for details

and responsibilities.

IUP CONFINED SPACE ENTRY PERMIT

Date and Time Issued:			  Date and Time Expires:

Job Site/Space I.D.:				  Job Supervisor:

Work to be Performed:

Unit Manager:

Unit Supervisor:

Safety Observer:

1.	Atmospheric Checks:		Time

O2			%

LEL			%

CO			ppm

H2S			ppm

2.	Tester’s Signature:

3.	Source isolation (No entry):	N/A	Yes	No

Pumps or lines blinded,		(    )	(    )	(    )

Disconnected, or blocked		(    )	(    )	(    )

4.	Ventilation Modification:		N/A	Yes	No

Mechanical				(    )	(    )	(    )

Natural Ventilation Only		(    )	(    )	(    )

5.	Atmospheric Check After

Isolation and Ventilation:

O2			%

LEL			%

CO			ppm

H2S			ppm

Time

Tester’s Signature:

6.	Radio Check Time:

7.	Rescue Procedures:*See attached Confined Space Rescue Procedures

8.	Supervisor, unit manager, safety			Yes	No

observer and entrants

successfully completed training?			(    )	(    )

9.	Equipment:					N/A	Yes	No

Direct reading gas monitor tested		(    )	(    )	(    )

Safety Harness and lifelines for

entry and standby persons			(    )	(    )	(    )

Hoisting equipment				(    )	(    )	(    )

Powered communications			(    )	(    )	(    )

All electric equipment listed Class 1,

Division 1, Group D and

Non-Sparking tools				(    )	(    )	(    )

10.	Periodic atmospheric tests:  *use attached chart

11.	Special conditions:

We have reviewed the work authorized by this permit and the information contained herein.  Written instructions and safety procedures have been received and are understood.  Entry cannot be approved if any squares are marked in the “No” column.  This permit is not valid unless all appropriate items are completed.

Permit Prepared By: (Supervisor)

Approved By: (Unit Supervisor)

Reviewed By: (Safety Observer)

(entrants)

(printed name)		(signature)

This permit is to be kept at the job site.  Return job site copies to Safety Office, Unit Supervisor and Unit Manager following job completion.

Emergency Medical Service	Safety Department		Campus Police

911			       357-5705		     357-2141

Periodic Atmospheric Tests. Job Site I.D.:		     Date:

| TIME | O2 | CO | LEL | H2S |
| --- | --- | --- | --- | --- |