HOW TO INSPECT RECHARGEABLE, PORTABLE, DRY CHEMICAL

FIRE EXTINGUISHERS

The IUP Department of Public Safety uses the following process of inspecting rechargeable, portable, dry chemical fire extinguishers.  According to the National Fire Protection Agency 101, an inspection is a quick check intended to give you reasonable assurance that an extinguisher is available, fully charged, and operable.  It is important to do a complete and thorough inspection to assure that the extinguisher operates properly in an emergency situation.  Inspect the extinguishers annually.  This process requires one person and will take approximately 2-3 minutes/extinguisher to complete.

The following list of supplies will be needed:

- Locking pin

- Plastic fastener

- Inspection record tag

- Wire tie

- Ink pen (preferably blue or black)

The inspection is done from the top of the extinguisher to the bottom in order to reduce the chance of omitting one of the steps.

MAKE SURE THE TYPE OF EXTINGUISHER IS SUITABLE.

The extinguisher furnished needs to be able to cope with the kind of fires 	anticipated in the property or area protected.  The following is a list and 	explanation of the different classes of fires.

- CLASS A-fire in ordinary combustible materials, such as wood, cloth, paper, rubber and many plastics.

- CLASS B-fires in flammable liquids, gases, and greases.

- CLASS C-fires that involve energized electrical equipment where the electrical non-conductivity of the extinguishing medium is of importance.

- CLASS D-fires in combustible metals, such as magnesium, titanium, zirconium, sodium and potassium.

The type of the extinguisher will be marked on the shell of the extinguisher.  The shell is the outer-casing of the extinguisher.

MAKE SURE THE EXTINGUISHER IS READILY ACCESSIBLE.

The first extinguisher should be at a reasonable height from the floor so 	that the average person is able to reach it (the average person is 	considered to be 5 feet 6 inches).  In order to ensure that the extinguisher 	is visible and accessible; remove any objects that may be blocking it, such 	as furniture, machinery, etc.

MAKE SURE THE EXTINGUISHER IS WELL CARED FOR.

Do a general overview of the extinguisher to assure there is no dust or dirt 	coating the shell.  Check for corrosion and dents of the shell, which are 	signs of weakness.

MAKE SURE THE LOCKING PIN IS IN PLACE AND PROPERLY SECURED

The pin locks the discharge lever and keeps the extinguisher from being 	discharged accidentally.  The pin goes through the holes of the discharge 	lever and carrying lever.  Once the pin is in place, secure it with the plastic 	fastener.  To do this, put the fastener through the circle of the pin and 	wrap the fastener around the discharge lever.  Put the thin end of the 	fastener through the hole of the fastener that reads “ENTER” and pull the 	fastener through.  The pin is now secured until the fastener is intentionally 	broken.

MAKE SURE THE EXTINGUISHER IS PROPERLY CHARGED.

Properly charged means that the powder is under a certain 	pressure/square inch.  An extinguisher needs enough charge so that when 	it is discharged, there is an ample amount of dry chemical with a velocity 	sufficient enough to propel the chemical 10-20 feet.  The range of a 	properly charged extinguisher is between 185-205 p.s.i.  This value is 	displayed on the pressure gauge.  If the extinguisher is properly charged, 	the dial of the pressure gauge will be in the green section.  A reading 	below 185 p.s.i. is considered undercharged which may be an indication 	that the extinguisher was discharged or leaking.  It may not have sufficient 	powder to properly extinguish a fire.  The dial of the pressure gauge will 	be below the green section.  If the gauge reads above 205 p.s.i., the 	extinguisher is overcharged and the dial will be above the green section.  	An overcharged extinguisher may not interfere with the discharge process, 	but it may damage the gaskets of the hose and cause leakage.

MAKE SURE THE HOSE IS NOT DAMAGED OR DETERIORATED.

Check the connection between the hose and shell to make sure they are 	secure.  If the connection is not secure, the extinguisher may leak.  Check 	the hose for any cracks or thin spots, which may also cause leakage.  	Check the nozzle to see that it is clear and unobstructed from objects such 	as paper, gum, etc.  If there is a blockage of the nozzle, this may cause a 	pressure build-up in the hose and restrict the powder from being released.

MAKE SURE THE HYDROSTATIC TESTING IS UP-TO-DATE.

Hydrostatic testing is the process of removing all traces of water and 	moisture from the inside of the extinguisher.  This is to protect against 	unexpected in-service failure. CAUTION:  Hydrostatic testing is 	considered a maintenance job and is to be done by an independent 	testing laboratory.  During inspection, your responsibility is to check that 	the testing has been updated. The month and year of the last hydrostatic 	testing is imprinted on the bottom of the foot ring or on a sticker on 	the 	shell.  Hydrostatic testing needs to be completed every twelve years.

MAKE SURE THE HANGER IS FASTENED SOLIDLY.

The extinguisher needs to be mounted on a hanger.  If the extinguisher is 	sitting on the floor, it may be knocked over.  The cap may break off 	causing an intense release of pressure that may provoke the cap to act as 	a projectile.  The hanger needs to be securely fastened to the wall so it 	does not break free causing the extinguisher to fall to the floor.

MAKE SURE THERE IS AN INSPECTION RECORD ATTACHED TO THE EXTINGUISHER.

An inspection record card needs to be attached to the extinguisher with a wire tie.  It should be affixed where it is easily accessible so that it does    not hinder operation.  Some locations include around the neck or the gauge.  Mark on the card the date of inspection, finding and your initials.